## Slide 1: Online Optimization for Power Networks
Changhong Zhao
Lingwen Gan
Steven Low
EE, CMS, Caltech
January 2016
Enrique Mallada
ME, Johns Hopkins
Notes: May 2012: Santa Fe Institute Workshop on Smart Grid, Santa Fe, NM
July 2012: Network Science Workshop, Chinese University of Hong Kong, HK (Raymond Yeung)
Sept 2012: Melbourne University, EEE Department (Pascal van Hentenryck)
February 13, 2013: ITA Workshop, San Diego
May 20, 2013: IEEE Workshop on Modeling and Simulation of Cyber-Physical Energy Systems, Berkeley, CA (Peter Palensky, Edward A. Lee)
Oct 31, 2013: Google, Mountain View, CA (Arun Mazumdar)
Nov 5, 2013: Asilomar Conference, invited session on Power Networks (Edmund Yeh)
Nov 15, 2013: NSF Workshop on Smart Grid, Washington DC (Giannakis, Sairaj, SL)
Dec 2, 2013: UCLA EE (Mani Srivastava)
Dec 5, 2013: Keynote, GlobalSIP (Global Conf on Signal & Info Processing) Symposium on Signal Processing in Smart Grid (Shalinee Kishore, Lalitha Sankar)
Jan 16, 2014: Stanford Smart Grid seminar (Ram Rajagopal, Baosen Zhang)
Feb 4, 2014: 9th Annual CARNEGIE MELLON CONFERENCE ON THE ELECTRICITY INDUSTRY, (Marija Ilic, Krishnan Kant)
May 22, 2014: UC Berkeley (Kameshwar)
Oct 3, 2014: ASU (Junshan Zhang)
Nov 3, 2014: Asilomar Conference, invited session on Smart Grid: learning and optimization, Pacific Grove, CA
Nov 10, 2014: EE Control Group, Berkeley (Claire Tomlin)
Jan 16, 2015, Grid Science Winter School and Conference (Scott Backhaus, Misha Chertkov)
June 9, 2015: Advanced Mathematical Methods For Energy Systems: from Theory to Practice, Moscow, Russia (Janusz Bialek, Skoltech)
July 7, 2015, Tsinghua power systems group (Prof Song Yonghua)
July 21, 2015: Hong Kong University, EEE (David Hill, Victor Li)
Online algorithms
=============
Jan 14, 2016: IPAM Workshop on Optimization and Equilibrium of Energy Economics, UCLA, CA (Mike Ferris)
Jan 28, 2016: ESIF Workshop on Frontiers in Distributed Optimization and Control of Sustainable Power Systems, NREL, Golden, CO

## Slide 2: Key message
Large network of DERs
  Real-time optimization at scale
Online optimization
  Network solves hard problems in real time for free
  Exploit it for our optimization/control
  Naturally adapts to evolving network conditions
Examples
  Slow timescale: OPF
  Fast timescale: frequency control

## Slide 3: Outline
Optimal power flow
  DistFlow model and ACOPF
  Online algorithm
  Analysis and simulations
Load-side frequency control
  Dynamic model & design approach
  Distributed online algorithm
  Analysis and simulations
  Details
Main references (frequency control):
Zhao, Topcu, Li, Low, TAC 2014
Mallada, Zhao, Low, Allerton 2014
Zhao, Low, CDC 2014, Zhao et al CISS 2015

## Slide 4: Bus injection model
Power flow equations
OPF = QCQP  SDP relaxation

## Slide 5: Branch flow model
j
k
directed graph G

## Slide 6: Branch flow model
linear
quadratic
DistFlow equations (radial nk)
Baran & Wu, 1989

## Slide 7: Branch flow model
Branch flow model
Bus injection model
DistFlow equations (radial nk)
Baran & Wu, 1989

## Slide 8: Branch flow model
Branch flow model
Bus injection model
+ cycle condition on

## Slide 9: Cycle condition
A relaxed solution satisfies the cycle condition if
incidence matrix;
depends on topology

## Slide 10: Branch flow model
Branch flow model
Bus injection model
+ cycle condition on
[Farivar & Low 2013 TPS
Bose et al 2012 Allerton]
Theorem: BIM = BFM

## Slide 11: Branch flow model
BFM and BIM are equivalent (nonlinear bijection)
… but some results are easier to formulate or
prove in one than the other
BFM is much more numerically stable
BFM is useful for radial networks
  Extremely efficient computation (BFS)
  Much better linearization
  Compact extension to multiphase unbalanced nk

## Slide 12: SOCP relaxation
SOC relaxation of BFM
Bus injection model

## Slide 13: SOCP relaxation of OPF

## Slide 14: Sufficient conds for exact relaxation
Tutorial: Convex relaxation of OPF, IEEE Trans. Control of Network Systems, 2014
For mesh networks, see recent works of Andy Sun, Pascal van Hentenryck on
relaxation of cycle condition

## Slide 15: Sufficient conds for exact relaxation
Tutorial: Convex relaxation of OPF, IEEE Trans. Control of Network Systems, 2014
For mesh networks, see recent works of Andy Sun, Pascal van Hentenryck on
relaxation of cycle condition

## Slide 16: SOCP relaxation of OPF
But all these algorithms are offline …
… unsuitable for real-time optimization
network of distributed energy resources

## Slide 17: OPF
F(x, y) = 0
BFM
controllable devices

## Slide 18: OPF
F(x, y) = 0
BFM (DistFlow, radial network)
controllable devices

## Slide 19: Approximate OPF
Recap
Reduce to x only
Add barrier function
on v(x)
L: nonconvex

## Slide 20: Online gradient algorithm
gradient projection algorithm:
Explicitly exploits network to carry out part of algorithm
Naturally tracks changing network conditions
active control
law of physics

## Slide 21: Online gradient algorithm
gradient projection algorithm:
active control
law of physics
Results
Local optimality
Global optimality
Suboptimality bound
[Gan & Low 2016 JSAC]

## Slide 22: Local optimality
  x(t) converges to set of local optima
  if #local optima is finite, x(t) converges

## Slide 23: Global optimality
Theorem
If all local optima are in A then
  x(t) converges to the set of global optima
  x(t) itself converges a global optimum

## Slide 24: Global optimality
Theorem
  If SOCP is exact over X, then assumption holds

## Slide 25: Suboptimality gap
  Informally, a local minimum is almost as good
  as any strictly interior feasible point
local
optimum
any original
feasible pt
slightly away
from boundary

## Slide 26: Simulations

## Slide 27: Outline
Optimal power flow
  DistFlow model and ACOPF
  Online algorithm
  Analysis and simulations
Load-side frequency control
  Dynamic model & design approach
  Distributed online algorithm
  Analysis and simulations
  Details
Main references (frequency control):
Zhao, Topcu, Li, Low, TAC 2014
Mallada, Zhao, Low, Allerton 2014
Zhao, Low, CDC 2014, Zhao et al CISS 2015

## Slide 28: Motivation
2011 Southwest blackout
(1 min)
  All buses synchronized to same nominal frequency (US: 60 Hz; Europe/China: 50 Hz)
  Supply-demand imbalance  frequency fluctuation

## Slide 29: Motivation
Imagine when we have 50%+ renewable generation …
(1 min)
(10 min)

## Slide 30: Why load-side participation
sec
min
5 min
60 min
primary
freq control
secondary freq control
economic
dispatch
Ubiquitous continuous load-side control can supplement generator-side control
  faster (no/low inertia)
  no extra waste or emission
  more reliable (large #)
  better localize disturbances
  reducing generator-side control capacity

## Slide 31: What is the potential
US:
operating reserve: 13% of peak
total GFA capacity: 18%
Lu & Hammerstrom (2006), PNNL
Residential load accounts
for ~1/3 of peak demand
61% residential appliances
are Grid Friendly

## Slide 32: How
How to design load-side frequency control ?
How does it interact with generator-side control ?

## Slide 33: Literature: load-side control
Original idea & early analytical work
  Schweppe et al 1980; Bergin, Hill, Qu, Dorsey, Wang, Varaiya …
Small scale trials around the world
  D.Hammerstrom et al 2007, UK Market Transform Programme 2008
Early simulation studies
  Trudnowski et al 2006, Lu and Hammerstrom 2006, Short et al 2007, Donnelly et al 2010, Brooks et al 2010, Callaway and I. A. Hiskens, 2011, Molina-Garcia et al 2011
Analytical work – load-side control
  Zhao et al (2012/2014), Mallada and Low (2014), Mallada et al (2014), Zhao and Low (2014), Zhao et al (2015)
  Simpson-Porco et al 2013, You and Chen 2014, Zhang and Papachristodoulou (2014), Ma et al (2014), Zhao, et al (2014),
Recent analysis – generator-side/microgrid control:
  Andreasson et al (2013), Zhang and Papachristodoulou (2013), Li et al (2014), Burger et al (2014), You and Chen (2014), Simpson-Porco et al (2013), Hill et al (2014), Dorfler et al (2014)

## Slide 34: Network model
generation
loads:
controllable + freq-sensitive
i : region/control area/balancing authority
branch power
Will include generator-side
control later

## Slide 35: Network model
Generator bus: Mi > 0
Load bus: Mi = 0
Damping/uncontr loads:
Controllable loads:

## Slide 36: Network model
swing dynamics
all variables are deviations
from nominal
extends to nonlinear power flow

## Slide 37: Frequency control
Suppose the system is in steady state
Then: disturbance in gen/load …

## Slide 38: Frequency control
current
approach
load-side
control

## Slide 39: Outline
Network model
Distributed online algorithm
Simulations
Details
Main references:
Zhao, Topcu, Li, Low, TAC 2014
Mallada, Zhao, Low, Allerton 2014
Zhao, Low, CDC 2014, Zhao et al CISS 2015

## Slide 40: Load-side controller design
Control goals (while min disutility)
  Rebalance power & stabilize frequency
  Restore nominal frequency
  Restore scheduled inter-area flows
  Respect line limits
Zhao, Topcu, Li, Low
TAC 2014
Mallada, Zhao, Low
Allerton, 2014

## Slide 41: Load-side controller design
Control goals (while min disutility)
  Rebalance power & stabilize frequency
  Restore nominal frequency
  Restore scheduled inter-area flows
  Respect line limits
Zhao, Topcu, Li, Low
TAC 2014
Mallada, Zhao, Low
Allerton, 2014

## Slide 42: Load-side controller design
Design control law
whose equilibrium
solves:
power balance
inter-area flows
line limits
Control goals (while min disutility)
  Rebalance power & stabilize frequency
  Restore nominal frequency
  Restore scheduled inter-area flows
  Respect line limits
load disutility
freq will emerge as
Lagrange multiplier
for power imbalance

## Slide 43: Load-side controller design
Design control (G, F) s.t. closed-loop system
  is stable
  has equilibrium that is optimal
power network
load control

## Slide 44: Load-side controller design
Idea: exploit system dynamic as part of primal-dual algorithm for modified opt
  Distributed algorithm
  Stability analysis
  Control goals in equilibrium
power network
load control

## Slide 45: Summary: control architecture
Primary load-side frequency control
completely decentralized
Theorem: stable dynamic, optimal equilibrium
Zhao, Topcu, Li, Low. TAC 2014
physical network

## Slide 46: Summary: control architecture
Mallada, Zhao, Low. Allerton 2014
Secondary load-side frequency control
communication with neighbors
Theorem: stable dynamic, optimal equilibrium
physical network
cyber network

## Slide 47: Summary: control architecture
With generator-side control, nonlinear power flow
load-side improves both transient & eq
Theorem: stable dynamic, optimal equilibrium
Zhao, Mallada, Low. CISS 2015
physical network
cyber network

## Slide 48: Outline
Network model
Load-side frequency control
Simulations
Details
Main references:
Zhao, Topcu, Li, Low, TAC 2014
Mallada, Zhao, Low, Allerton 2014
Zhao, Low, CDC 2014, Zhao et al CISS 2015

## Slide 49: Local frequencies
[Tom Overbye, 2015 Cornell]

## Slide 50: Simulations
Dynamic simulation of IEEE 39-bus system
Power System Toolbox (RPI)
Detailed generation model
Exciter model, power system
stabilizer model
Nonzero resistance lines

## Slide 51: Primary control

## Slide 52: Secondary control
swing dynamics
with OLC
area 1

## Slide 53: Secondary control
no line limits
with line limits
Total inter-area flow is
the same in both cases
line limit
line limit

## Slide 54: Key message
Large network of DERs
  Real-time optimization at scale
Online optimization
  Network solves hard problems in real time for free
  Exploit it for our optimization/control
  Naturally adapts to evolving network conditions
Examples
  Slow timescale: OPF
  Fast timescale: frequency control

## Slide 55
more details
(backup)

## Slide 56: Outline
Network model
Load-side frequency control
Simulations
Details
Main references:
Zhao, Topcu, Li, Low, TAC 2014
Mallada, Zhao, Low, Allerton 2014
Zhao, Low, CDC 2014, Zhao et al CISS 2015

## Slide 57: Recall: design approach
Idea: exploit system dynamic as part of primal-dual algorithm for modified opt
  closed-loop system is stable
  its equilibria are optimal
power network
load control

## Slide 58: Outline
Load-side frequency control
  Primary control
  Secondary control
  Interaction with generator-side control
Zhao et al SGC2012, Zhao et al TAC2014

## Slide 59: Optimal load control (OLC)
demand = supply
disturbances
controllable
loads

## Slide 60: system dynamics + load control = primal dual alg
swing dynamics
load control
active control
implicit

## Slide 61: Control architecture

## Slide 62: Load-side primary control works
Theorem
Starting from any
system trajectory
converges to
  is unique optimal of OLC
  is unique optimal for dual
completely decentralized
frequency deviations contain right info for local decisions that are globally optimal

## Slide 63: Recap: control goals
  Rebalance power
  Stabilize frequencies
  Restore nominal frequency
  Restore scheduled inter-area flows
  Respect line limits
Yes
Yes
No
No
No

## Slide 64: Outline
Load-side frequency control
  Primary control
  Secondary control
  Interaction with generator-side control
Mallada, Low, IFAC 2014
Mallada et al, Allerton 2014

## Slide 65: OLC for secondary control
restore nominal freq
demand = supply

## Slide 66: OLC for secondary control
key idea: “virtual flows”
demand = supply
in steady state:
virtual flow = real flows
restore nominal freq

## Slide 67: OLC for secondary control
restore nominal freq
in steady state:
virtual flow = real flows
restore inter-area flow
respect line limit
demand = supply

## Slide 68: Recall: primary control
swing dynamics:
load control:
active
control
implicit

## Slide 69: Control architecture
physical network
cyber network

## Slide 70: Secondary frequency control
load control:
computation & communication:
primal var:
dual vars:

## Slide 71: Secondary control works
Theorem
starting from any initial point, system
trajectory converges s. t.
  is unique optimal of OLC
  nominal frequency is restored
  inter-area flows are restored
  line limits are respected

## Slide 72: Recap: key ideas
Design optimal load control (OLC) problem
  Objective function, constraints
Derive control law as primal-dual algorithms
  Lyapunov stability
  Achieve original control goals in equilibrium
Distributed algorithms
primary control:
secondary control:

## Slide 73: Recap: key ideas
Design optimal load control (OLC) problem
  Objective function, constraints
Derive control law as primal-dual algorithms
  Lyapunov stability
  Achieve original control goals in equilibrium
Distributed algorithms
Virtual flows
  Enforce desired properties on line flows
in steady state: virtual flow = real flows

## Slide 74: Recap: control goals
  Rebalance power
  Resynchronize/stabilize frequency
  Restore nominal frequency
  Restore scheduled inter-area flows
  Respect line limits
Yes
Yes
Secondary control restores nominal
frequency but requires local communication
Yes
Yes
Mallada, et al Allerton2014
Zhao, et al TAC2014
Yes

## Slide 75: Outline
Load-side frequency control
  Primary control
  Secondary control
  Interaction with generator-side control
Zhao and Low, CDC2014
Zhao, Mallada, Low, CISS 2015

## Slide 76: Generator-side control
Recall model: linearized PF, no generator control
New model: nonlinear PF, with generator control

## Slide 77: Generator-side control
generator bus: real power injection
load bus: controllable load
New model: nonlinear PF, with generator control

## Slide 78: Generator-side control
New model: nonlinear PF, with generator control
generator buses:

## Slide 79: Load-side control
physical network
cyber network

## Slide 80: Load-side primary control works
Theorem
Every closed-loop equilibrium solves OLC and its dual
Suppose
Any closed-loop equilibrium is (locally) asymptotically stable provided

## Slide 81: Conclusion
Forward-engineering design facilitates
  explicit control goals
  distributed algorithms
  stability analysis
Load-side frequency regulation
  primary & secondary control works
  helps generator-side control